## GWRC
GREATER WELLINGTON REGIONAL COUNCIL (GWRC)
Water Type | DIA # | Performance Measure | Target | End of Year Result | Q1 25/26 Result | Result Comments / Explanation
Water supply | 1A | The extent to which the local authority’s drinking water supply complies with the following parts of the drinking water quality assurance rules for each water treatment plant: · T3 Bacterial Rules (GWRC WTPs) Part H - Gear Island, Te Marua, Wainuiomata, Waterloo · T3 Protozoal Rules (GWRC WTPs) Part I - Gear Island, Te Marua, Wainuiomata, Waterloo · D3 Distribution (Microbiological Monitoring) Rules (Part J) - GWRC bulk water network | All Met (100%) |  | 98% | The Waterloo Water Treatment Plant is non-compliant with the new Drinking Water Quality Assurance rules due to insufficient contact time with chlorine for water for approximately 800 households. Funding has been provided by Hutt City Council in their Long-Term Plan to address this issue, and the water remains safe to drink.
Water supply | 2 | The percentage of real water loss from the local authority’s networked reticulation system | +/- 0.25% |  | 0.11% | Approx. 15 ML of Non Revenue Water estimated in Q1 : -About 4.7 ML scoured from new Silverstream bridge/branch valves installation project; -About 4.1 scoured from the installation of the first seismic coupler at the rocky point chamber project; -About 1.8 MLD of NRW as Churton park reservoir had valve control issues resulting in overflow; -The remaining 4.4ML scoured from WTPs regular maintainance operations.
Water supply | 3A | Median response time to attend urgent call-outs | <90 mins |  | 0 | No Event.
Water supply | 3B | Median response time to resolve urgent call-outs | <8 hours |  | 0 | No Event.
Water supply | 3C | Median response time to attend non-urgent call-outs | <72 hours |  | 0 | No Event.
Water supply | 3D | Median response time to resolve non-urgent call-outs | <20 days |  | 0 | No Event.
Water supply | 4 | The total number of complaints received about drinking water taste, clarity, odour, water pressure or flow, continuity of supply or the response to any of these issues; expressed per 1000 connections | <0.2 |  | N/A | We can't measure this currently due to system limitations
Water supply | 5 | Average consumption of drinking water per day per resident | <375L |  | 372.6 | Significant demand reduction achieved in last 12 months thanks to increased investment from city councils in finding and fixing leaks.
Water supply | LTP | Number of waterborne disease outbreaks | 0 |  | 0
Water supply | LTP | Sufficient water is available to meet normal demand except in a drought with a severity of greater than or equal to 1 in 50 years | <2% |  | 0.9% | The Wellington metropolitan water supply has returned to achieving the water shortage level of service. This is due to a significant reduction in network water loss and an increase in supply capacity following completion of the Te Marua WTP Optimisation project. The risk is assessed as the likelihood of reaching Level 4 restrictions (refer Water Shortage Risk Management Plan).

## Drinking Water Compliance
The extent to which the local authority’s drinking water supply complies with the following parts of the drinking water quality assurance rules:
T3 Bacterial Rules (GWRC Treatment Plants) (Part H)
Plant | YTD compliance | Q1 Compliance | Commentary
Gear Island | All Met (100%) | All Met (100%)
Te Mārua | All Met (100%) | All Met (100%)
Wainuiomata | All Met (100%) | All Met (100%)
Waterloo | Partially Met (91.67%) | Partially Met (91.67%) | The Waterloo Water Treatment Plant remains non-compliant with the relevant treatment rules due to insufficient contact time with chlorine for approximately 800 households in Lower Hutt, closest to the Plant. Projects underway to allow closure of cross connections which once complete will achieve 100% compliance
T3 Protozoal Rules (GWRC Treatment Plants) (Part I)
Gear Island | All Met (100%) | All Met (100%)
Te Mārua | All Met (100%) | All Met (100%)
Wainuiomata | All Met (100%) | All Met (100%)
Waterloo | All Met (100%) | All Met (100%)
D3 Distribution (Microbiological Monitoring) Rules (Part J)
GWRC Bulk Water Network | All Met (100%) | N/A | Bulk water is not a distribution zone.